| Date: | 19/07/2025 | Deviation No. | DEV/PR/25/003 |
| --- | --- | --- | --- |
| Investigation tool used: 6M 5 Why Brainstorming |  |  |  |
| Other Tools (If any): |  |  |  |
| Not applicable |  |  |  |
| Define: |  |  |  |
| Following checks shall be considered while writing the “Define” section. - Clearly define what happens actually. - Explain what is different than expected. - Mention the location where the deviation has occurred. - Date/time of deviation occurrence and date/time of detection. - Mention the name of personnel who is involved in the deviation. - Mention initial scope of deviation (i.e., impacted product/Material/Equipment/System/Batches/etc.) On 10/04/2025 at approximately 16:30 hrs, during the execution of the Audit Trail Review (ATR) sheet by a QA colleague (Employee ID: 893) in the SCADA Room (GF-93), it was observed that the audit trail report for the period 01/03/2025 to 31/03/2025 was not visible on the SCADA system. Subsequently, on 15/05/2025, during the Audit Trail Review (ATR) sheet execution for the month of April 2025, the same QA colleague (Employee ID: 893) again identified that the audit trail report for the period 01/04/2025 to 30/04/2025 was also not visible on the SCADA system. To investigate and resolve the issue, Work Order No. WO/PR/25-024 was raised on 17/05/2025. However, the audit log data could not be retrieved. As a result, a deviation has been logged to identify the root cause of the issue. |  |  |  |
| Details Investigation: |  |  |  |
| Measure: Following checks shall be considered while writing the “Measure” section. - Does the summary provide relevant facts and data/information that was reviewed including: environment, process/product history, personnel info (title and job title), controls limits, etc. - Is a summary of the analysis of the factors and data provided? - Is a conclusion statement of the analysis and review provided? - If there were Regulatory Notification, were details provided? - Is the report written in a logical flow and easily understood by the reader? As per the Standard Operating Procedure (SOP No. SOP/DP/QA/029-R00) "review of audit trial data)," point no. 7.12 audit trial shall be review Starting of each month (within 15 working days). During review of audit trial data on 10/04/25 , QA colleague (Employee ID: 893) observed that audit trial report was not visible on SCADA system for the period of 01/03/25 to 31/03/25. After identification of nonconformance the issue was communicated to OEM (TEMA SINERGIE) however due to incidence occurred at M.J. Biopharm Pune (DEV/QC/25/001) all activities are halted. Subsequently, on 15/05/2025, during the Audit Trail Review (ATR) sheet execution for the month of April 2025, the same QA colleague (Employee ID: 893) again identified that the audit trail report for the period 01/04/2025 to 30/04/2025 was also not visible on the SCADA system. To resolve the issue, Work Order No. WO/PR/25-024 was raised on 17/05/2025 to IT department. As per IT Assessment on work order, OEM support required. Hence, remote access form initiated system given on remote access to OEM. During investigation OEM identified that IFIXALARMS table reached full capacity, which prevented the system from generating and saving new Audit trails. Also, it was identified that scheduled cleanup task was not functioning correctly. During the remote session on 27/05/25, OEM resolved the issue as a result, the system is once again generating iFix Audit logs as expected. The cleanup task is now working properly and maintaining the database as intended. However, as per OEM service report, the Audit logs from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25 are unrecoverable due to the database being full during that time. After resolving the issue, audit log reports verified and found satisfactory. The process/operation data and reports are in place and there is no any impact anticipated on routine operation. Based on these controls and observations, the missed data of audit log is not anticipated to have any impact on product quality or patient safety. The deviation is related to not available of audit log data for AGLTS. However, since there is no impact on product quality and safety, regulatory notification is not required. |  |  |  |
| Analyze: Various investigation tools used to analyze the root cause like 6M, 5 Why, Personnel interview, Brainstorming etc. |  |  |  |
| 6 M Method (If Applicable): - Man: Not Applicable. - Machine: Not Applicable. - Measurement: Not Applicable. - Material: Not Applicable. - Method: Not Applicable. - Milieu (Environment): Not Applicable. Conclusion Not Applicable |  |  |  |
| Note: No 6 M question shall be deleted in the investigation, If any question is not applicable, then mention in ans. as “Not Applicable”. |  |  |  |
| 5 Why Approach (If Applicable): 1. WHY: Why remote access form Initiated for AGLTS? Ans. Remote access form initiated for AGLTS because of a requirement from IT department. 2. WHY: Why IT department required remote access form? Ans. IT department required a remote access form because work order No. WO/PR/25/-024 raised to IT department. 3. WHY: Why was the work order No. WO/PR/25-024 raised to IT department? Ans. Work order No. WO/PR/25-024 is raised to IT department because Audit log was not visible in the AGLTS SCADA System. 4. WHY: Why was audit log not visible in the SCADA System? Ans. Audit log was not visible in the SCADA System because audit log data was not generated in the SCADA System. 5. WHY: Why was audit log data not generated in the SCADA System? Ans. Audit log data was not generated in the SCADA System because IFIXALARMS table reached full capacity. 6. WHY: Why was the IFIXALARMS table reached full capacity? Ans. IFIXALARMS table reached full capacity because IFIXALARMS table prevented the system from generating and saving new Audit trails. - WHY: Why was the IFIXALARMS table prevented the system from generating and saving the new audit trails? Ans. IFIXALARMS table prevented the system from generating and saving the new audit trails because scheduled cleanup task was not functioning correctly. Conclusion: Based on the 5 Whys analysis, it is concluded that the deviation occurred due to scheduled cleanup task was not functioning as per its intended use which lead to prevent the system from generating and saving new Audit trails ultimately resulting in nonconformance. |  |  |  |
| Brainstorming: Not Applicable |  |  |  |
| Other Tool if Any: Not Applicable |  |  |  |
| Other Tool if Any: Not Applicable |  |  |  |
| Investigation Outcome: |  |  |  |
| The investigation has been carried out by using the DMAIC and 5 Why methodology. The deviation is categorized as “minor” hence preliminary investigation was not performed. The nonconformance occurred due to audit trial data was not visible for the period from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. During investigation, it was observed that cleanup task was not functioning correctly due to which IFIXALARMS table reached full capacity due to which audit log was not generated. Also, it is identified that the Audit logs from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25 are unrecoverable due to the database being full during that time. Also, the process/operation data and reports are in place and there is no any impact anticipated on routine operation. As per OEM service report, the cleanup task is now working properly and maintaining the database as intended and the user will not experience this issue again. Based on these controls and observations, the missed data of audit log is not anticipated to have any impact on product quality or patient safety. Based on the nature of non-conformance, a chronology of event, and detailed investigation, further root cause categorization has been done as per format for “Root Cause Categorization” SOP/DP/QA/008-F04 and root cause for the non-conformance was identified as ‘Equipment/Instrument. |  |  |  |
| Identified Root Cause/ Probable Cause: |  |  |  |
| Based on the detailed investigation, the most probable root cause as mentioned below - Primary Root Cause Level 1: Equipment. 2. Secondary Root Cause Level 2: Computer system. 3. Third Root Cause Level 3: Not Applicable. |  |  |  |
| Impact Assessment (System/ Document/ Product/ Equipment/Patient safety/Past batches): |  |  |  |
| System: The nonconformance is related to audit log for AGLTS was not generated from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. The process/operation data and reports are in place and reports are attached with each batch. Against work order no. WO/PR/25-024, OEM resolved the issue. As a result, the system is once again generating iFix Audit logs as expected. After resolving the issue, audit log reports verified and found satisfactory and hence, there is no any impact anticipated on system operation. Document: The nonconformance is related to audit log for AGLTS was not generated from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. After closure of deviation, deviation number to be update in audit trail review (ATR) checklist. Product: The nonconformance is related to audit log for AGLTS was not generated from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. The process/operation data and reports are in place and reports are attached with each batch. Hence, it does not have impact on product. Equipment: The nonconformance is related to audit log for AGLTS was not generated from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. The process/operation data and reports are in place and reports are attached with each batch. After resolving the issue, audit log reports verified and found satisfactory. Hence it does not have any impact on equipment operation and the equipment was working as intended. Patient safety / Past Batches: The nonconformance is related to audit log for AGLTS was not generated from 31/01/25 to 26/02/25 and 29/03/25 to 26/05/25. The process/operation data and reports are in place and reports are attached with each batch. Hence, it does not have an impact on patient safety/past batches. |  |  |  |
| Improve: Improve section covers the corrective actions Following checkpoint shall be considered as guidance only while finalizing the corrective actions, - Is a specific corrective Actions identified (including applicable Immediate Actions) to remediate the current issue or situation such that the associated system was returned to a state of control/compliance and also it will avoid the recurrence of deviation? - Is specific Corrective Actions identified for each root cause /substantiated probable root cause, as applicable? - Is the Corrective action assigned a unique number, responsible person and due date so it can be tracked? Does the action describe what will be the expected outcome they can be verified? - Are the identified corrective actions achievable based on the information provided? |  |  |  |
| Corrective Action: |  |  |  |
| After identified of nonconformance, information given to production head and QA head and deviation DEV/PR/25/001 is initiated. However, to avoid the recurrence following corrective action is proposed, 1.Work Order no. WO/PR/25-024 raised to resolve the issue. Against work order, issue resolved and system is working as per its intended use hence there is no requirement of Corrective Action. |  |  |  |
| Control: Control section covers the preventive actions Following checkpoint shall be considered while finalizing the preventive actions, - Were specific Preventive Actions identified for each root cause /substantiated probable root cause as applicable? - Was the Preventive Action linked the classification of the root cause and explanation given for how it will prevent recurrence? - Was the Preventive action assigned a unique number, responsible person and due date so it can be tracked? Does the action describe and expected outcome can be verified? - Was Effectiveness Verification required or not and the rationale for either documented based on the quality impact of the incident after the investigation concluded? - Was an Interim Plan needed to ensure a state the control while the Preventive Actions were implemented? - Was rationale provided when no Preventive Action were identified? - Does the Final Comments section include rotational to support the conclusion of the investigation and CAPA. - Was each of the impact assessment fields completed correctly - Regulatory Impact, Regulatory notification Product Quality, Validation, Stability, Market/Clinical? - Does the Recommended Lot disposition match the conclusions of the investigation and Impact assessment? - Does the Conclusion include final decision and rationale other regulatory notification required? - CAPA required to release material or batches have been verified to be complete and closed prior to material or batch disposition. Any related CAPA that remain open, but have no impact on the material or batch release and a documented explanation is provided. - Does the Conclusion include a brief summary of root cause, final scope/impact including rationale for product/material disposition, impact assessment and relevant lot/material/equipment details? - Are the identified preventive actions achievable based on the information provided? |  |  |  |
| Preventive Action: |  |  |  |
| Following preventive actions proposed based on the outcome of the investigation. As per OEM service report the issue is resolved and will not experience the issue again. Hence no preventive action is proposed. |  |  |  |
| Document Reviewed: |  |  |  |
| - SOP/DP/QA/029 (Review of audit trial). - Audit trial review checklist. |  |  |  |
| List of attachment (If applicable): |  |  |  |
| Attachment No. I: Photocopy of work order. Attachment No. II: Photocopy of remote access form. |  |  |  |

| Prepared By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date | Approved By QA (Sign/Date) |
| --- | --- | --- | --- | --- | --- | --- |