| Date: | 03/04/2025 | Deviation No. | DEV/WH/24/004 |
| --- | --- | --- | --- |
| Investigation tool used: 6M 5 Why Brainstorming |  |  |  |
| Other Tools (If any): |  |  |  |
| Not applicable |  |  |  |
| Define: |  |  |  |
| Following checks shall be considered while writing the “Define” section. - Clearly define what happens actually. - Explain what is different than expected. - Mention the location where the deviation has occurred. - Date/time of deviation occurrence and date/time of detection. - Mention the name of personnel who is involved in the deviation. - Mention initial scope of deviation (i.e., impacted product/Material/Equipment/System/Batches/etc.) On 27/02/2025, while reviewing the temperature data logs for the approved RM walk-in cold room (Equipment Id: E/WH/020) and approved RM walk-in deep-freezer (Equipment Id: E/WH/021), data missing and temperature excursion were observed by a warehouse colleague (Employee ID: TR0160) . The temperature excursion was observed for the equipment Id: E/WH/020 (Temperature range: 2-8 ℃) from 20:34:07 to 22:48:45 and equipment Id: E/WH/021 (Temperature Range: -18 ℃ to -25 ℃) from 20:34:36 to 22:52:01. As per the site SOP No. SOP/DP/WH/016-R00 for “Operation and cleaning of Walk-in Cold Room and Walk-in Deep Freezer” point No. 7.4.2.2 stated that “Temperature shall be monitored through Kyoshi software in 1 min. and data shall be generated electronically and reviewed on daily basis by WH personnel same shall be approved by authorized personal as per access given” and at Point No. 7.2 “Temperature operating range is 2-8 ℃ for E/WH/020 and -18 ℃ to -25 ℃ for E/WH/021. However the temperature excursion and data missing were observed for both equipment, which is against the SOP No. SOP/DP/WH/016-R00. The nonconformance occurred on the ground floor (GF-30). As an immediate action, the nonconformance was informed to the Warehouse Head (Employee ID: 546) and the Quality Assurance Head (Employee ID: 288). At the time of nonconformance, protamine sulphate batch no. 523062 (2-8 ℃) was stored in the approved RM walk-in cold room (E/WH/020) and Insulin crystal Human (R-DNA) batch no. RHI24063 and RHI24065 (-18 ℃ or below) and Insulin glargine (IP/Ph.Eur) batch no. RIG23003-RP (-20 ± 5) were stored in the approved RM walk in the deep-freezer (E/WH/021). |  |  |  |
| Details Investigation: |  |  |  |
| Measure: Following checks shall be considered while writing the “Measure” section. - Does the summary provide relevant facts and data/information that was reviewed including: environment, process/product history, personnel info (title and job title), controls limits, etc. - Is a summary of the analysis of the factors and data provided? - Is a conclusion statement of the analysis and review provided? - If there were Regulatory Notification, were details provided? - Is the report written in a logical flow and easily understood by the reader? The approved RM walk-in cold room (Equipment ID: E/WH/020) and approved RM walk-in deep freezer (Equipment ID: E/WH/021) are used for the storage of raw materials and which are installed in the Approved RM Area (GF-30). The power supply of these room is provided by UPS as well as raw power. In UPS supply PLC & HMI are connected and compressor and overall equipment is connected on raw power. The UPS supply for both cold rooms has been provided from UPSDB-3, 4-Pole Main Incomer MCB, 63 Amps. From this UPS, power supply has been given to Dynamic pass box, RLAF, Door interlocking system, server rack, Cold room & deep freezer PLC & HMI panels. For more details refer the table-1, 2 and 3. During an investigation, it was identified that the Dynamic Pass Box (Equipment ID: E/PR/066) was in a shutdown condition. When the production colleague (Employee ID: 806) noticed this, they immediately informed the engineering team about the issue, and a concerned engineering person was assigned to address the problem. Upon visiting the service floor to assess the situation, the engineering colleague (Employee ID: 787) discovered that the UPSDB-3 (Uninterrupted Power Supply Distribution Board) located on the service floor, which has an incomer MCB of 63 Amps, had tripped. Refer to the below flow diagram for the UPSDB-3 power supply. Flow Diagram UPSDB-3 4-Pole Main Incomer MCB 63 Amps Y-Phase MCB 40 Amps B-Phase MCB 40 Amps R-Phase MCB 40 Amps B1 B2 B3 B4 B5 B6 B7 B8 – Cold Room & Deep Freezer B9 B10 Y1 Y2 Y3 Y4 Y5 Y6 – GF-33 (Decartoning Room) Y7 Y8 Y9 Y10 R1 R2 R3 R4 R5 R6 R7 – GF-77 (Pass Box) R8 R9 R10 Further investigation revealed that the main incoming power supply to UPSDB-3, rated at 63 Amps, had been divided into three phases: R-phase, Y-phase, and B-phase, each with an incomer of 40 Amps. During the inspection of the cable’s run from the UPSDB-3, it was noted that the insulation around the cable was damaged which was supplying UPS power to Dynamic pass, cold room & deep freezer (Refer attachment no. I). Due to this damaged condition of cables running UPSDB-3 was short circuit. Consequently, the MCB (Miniature Circuit Breaker) in the GF-33 decartoring area tripped (Y6 Phase, capacity: 20 Amps), which caused the Y-phase MCB (rated at 40 Amps) to trip as well. This chain of events led to the entire UPSDB-3 main incomer tripping, resulting in a power disruption. The compressor is used to maintain the temperature inside the cold room and deep freezer which is connected with PLC system through which command for auto Start / Stop of the compressor related to both equipment i.e., cold room & deep freezer. Due to short circuit at cables running from UPSDB-3 the power supply was interrupted which leads to the stoppage of compressor. Due to this series of event temperature excursion and data loss for Cold room & Deep freezer was occurred. Additionally, it has been observed that both the cold room PLC and HMI are connected with a UPS power supply that is connected in parallel with one. Refer to the table below for a detailed description of the three phases. Table – 1 (R-Phase) R-Phase; Equipment/System Name; Room No/Name. R1; Spare; NA. R2; Spare; NA. R3; Spare; NA. R4; Spare; NA. R5; Dynamic Pass Box; GF-52 Dispensing Room. R6; Spare; NA. R7; Dynamic Pass Box; GF-77 Garment Collection Room. R8; Spare; NA. R9; UPS Power Socket; GF-70 Part Washer Room, GF-69 Spare Room. R10; Spare; NA. Table-2 (Y-Phase) Y-Phase; Equipment/System Name; Room No/Name. Y-1; Spare; NA. Y-2; RLAF, UPS Socket; GF-25 Sampling Room, PPM Sampling Room. Y-3; Dynamic Pass Box; GF-53, Material Staging Room. Y-4; UPS Socket for RLAF-1; GF-52, Dispensing Room. Y-5; UPS Socket, PC Point; GF-30, Approved RM area, GF-29 Warehouse office. Y-6; Dynamic Pass Box; GF-33, De-Cartooning Room. Y-7; Dynamic Pass Box; GF-21, PPM Sampling Room. Y-8; UPS Socket; GF-132, Passage-II. Y-9; Door Interlocking system; Mezzanine area. Y-10; Above Ceiling Server Rack; Mezzanine area. Table-3 (B-Phase) B-Phase; Equipment/System Name; Room No/Name. B-1; Spare; NA. B-2; RLAF, UPS Point; GF-52 Dispensing Room. B-3; Spare; NA. B-4; Dynamic Pass Box; GF-25, RM Sampling Room. B-5; Spare; NA. B-6; LAF; GF-21, PPM Sampling Room. B-7; Spare; NA. B-8; Control Supply-Cold Room, Deep Freezer; GF-30, Approved RM area. B-9; Control Supply- Cold Room, Deep Freezer; GF-22, Under Test RM Cold Room. B-10; Spare; NA. Based on the above details, the power supply at MCB of B-phase and B8 was halted, which is connected to the walk-in cold room and walk-in deep freezer, leading to data loss in the approved RM walk-in cold room (equipment ID: E/WH/020) and approved RM walk-in deep freezer (equipment ID: E/WH/021). In impacted cold room & deep freezer below mentioned materials were stored refer the below tables, - Approved RM Walk-in Cold Room (E/WH/020) Sr. No.; Name of Material; Material Code; Product Batch No.; Available Qty.; Temperature Requirement. Protamine Sulphate; RI00056; 523062; 224.93 Gm; 2-8 °C. - Approved RM Walk-in Deep Freezer Room (E/WH/021) Sr. No.; Name of Material; Material Code; Product Batch No.; Available Qty.; Temperature Requirement. Insulin crystals (Human) (R-DNA); RA00468; RHI24063; 40.98 Gm; -18 °C or below. Insulin crystals (Human) (R-DNA); RA00468; RHI24065; 1260.202 Gm; -18 °C or below. Insulin Glargine (IP/Ph.Eur); RA00504; RIG23003-RP; 4.62888 GM; -20 ± 5°C.. Above mentioned materials stability study reports are available with us refer the below table. Sr. No.; Material Name; Report No.. Insulin crystals (Human) (R-DNA); QC/SR/RHI/022/IM/003. Insulin Glargine (IP/Ph.Eur); QC/SR/RIG/015/IM/006. Based on the above stability report it has been stated that, stability study was carried out for 3 months with 2-8 °C & it was observed that all the results are well within the defined limits. Hence there is no any impact on stored materials. |
| Analyze: Various investigation tools used to analyze the root cause like 6M, 5 Why, Personnel interview, Brainstorming etc. |  |  |  |
| 6 M Method (If Applicable): - Man: Not Applicable. - Machine: Not Applicable. - Measurement: Not Applicable. - Material: Not Applicable. - Method: Not Applicable. - Milieu (Environment): Not Applicable. Conclusion Not Applicable |  |  |  |
| Note: No 6 M question shall be deleted in the investigation, If any question is not applicable, then mention in ans. as “Not Applicable”. |  |  |  |
| 5 Why Approach (If Applicable): 1. WHY: Why was data loss observed in walk in cold room & walk in deep freezer? Ans. The supply to B8 MCB was not available. 2. WHY: Why was supply at B8-phase MCB was not available? Ans. Power supply at B-phase MCB was not available which is connected to walk in cold room & walk in deep freezer equipment. 3. WHY: Why was the power supply unavailable at the B-phase MCB? Ans. Main Incomer MCB at UPSDB-3 (Capacity: 63 Amps) was observed tripped. 4. WHY: Why Main incomer MCB was tripped? Ans. During the inspection of the cable running from the UPSDB-3 at Y6 phase, it was observed that the cable insulation was damaged. As a result, the MCB (Miniature Circuit Breaker) in the GF-33 decartoring area (Y6 Phase, capacity: 20 Amps) tripped, which in turn triggered the tripping of the Y-phase main MCB (rated at 40 Amps). This sequence of events ultimately led to the tripping of the entire UPSDB-3 main incomer 63 Amps. causing a power disruption. Conclusion: During 5 why tool, the main incoming power supply to UPSDB-3, rated at 63 Amps, had been divided into three phases: R-phase, Y-phase, and B-phase. During the inspection of the cable running from the main incomer of UPSDB-3 at Y6 phase, it was observed that the cable insulation was damaged, which caused the tripping at Y6 phase. As a result, the MCB (Miniature Circuit Breaker) in the GF-33 decartoring area (Y6 Phase, capacity: 20 Amps) tripped, which in turn triggered the tripping of the Y-phase MCB (rated at 40 Amps). This sequence of events ultimately led to the tripping of the entire UPSDB-3 main incomer, causing a power disruption. As a result of this incident, the MCB at B-phase (B8) also tripped, which is connected to the walk-in cold room and walk-in deep freezer, leading to data loss in the approved RM walk-in cold room (Equipment ID: E/WH/020) and approved RM walk-in deep freezer (Equipment ID: E/WH/021) *Note: Less or more than 5 questions may be asked based on the outcome of earlier questions. |  |  |  |
| Brainstorming: Not Applicable |  |  |  |
| Other Tool if Any: Not Applicable |  |  |  |
| Other Tool if Any: Not Applicable |  |  |  |
| Investigation Outcome: |  |  |  |
| The investigation has been carried out by using 5 Why tool. The investigation was driven through the 5 Why and personal interview was used to identify the root cause. The main incoming power supply to UPSDB-3, rated at 63 Amps, had been divided into three phases: R-phase, Y-phase, and B-phase. During the inspection of the cable running from the main incomer of UPSDB-3 at Y6 phase, it was observed that the cable insulation was damaged, which caused the tripping at Y6 phase. As a result, the MCB (Miniature Circuit Breaker) in the GF-33 decartoring area (Y6 Phase, capacity: 20 Amps) tripped, which in turn triggered the tripping of the Y-phase MCB (rated at 40 Amps). This sequence of events ultimately led to the tripping of the entire UPSDB-3 main incomer, causing a power disruption. As a result of this incident, the MCB at B-phase (B8) also tripped, which is connected to the walk-in cold room and walk-in deep freezer, leading to data loss in the approved RM walk-in cold room (Equipment ID: E/WH/020) and approved RM walk-in deep freezer (Equipment ID: E/WH/021). Based on the nature of nonconformance, a chronology of events, and a details investigation, further root cause categorization has been done as per format for “Root Cause Categorization” SOP/DP/QA/008-F04 |  |  |  |
| Identified Root Cause/ Probable Cause: |  |  |  |
| - Based on the detailed investigation, most probable root cause as mentioned below - Primary Root Cause Level 1: Equipment / Instrument. Secondary Root Cause Level 2: Electrical Failure. Third Root Cause Level 3: Not Applicable. |  |  |  |
| Impact Assessment (System/ Document/ Product/ Equipment/Patient safety/Past batches): |  |  |  |
| System: The deviation occurred due to the tripping of the entire UPSDB-3 main incomer 63 Amps. causing a power disruption. The air-handling units are functioning correctly, so there is no impact on the system. Document: The nonconformance about the temperature excursion and data loss of approved RM walk in cold room (Equipment ID: E/WH/020) and approved RM walk in deep-freezer (Equipment ID: E/WH/021). The equipment’s routine uses documents have been verified, and no abnormality was observed. Hence, there is no impact on the document. Product: The nonconformance is related to the temperature excursion and data loss of approved RM walk in cold room (Equipment ID: E/WH/020) and approved RM walk in deep-freezer (equipment Id: E/WH/021). At the time of nonconformance, protamine sulphate batch no. 523062 (2-8 ℃) was stored in the approved RM walk in cold room (E/WH/020) and Insulin crystal Human (R-DNA) batch no. RHI24063 and RHI24065 (-18 ℃ or below) and Insulin glargine (IP/Ph.Eur) batch no. RIG23003-RP (-20 ± 5) were stored in the approved RM walk in deep-freezer (E/WH/021). All stored materials accelerated stability data is available. Hence there is no impact on the product. Equipment: The nonconformance happened due to the tripping of the entire UPSDB-3 main incomer 63 Amps. causing a power disruption. Hence there is no impact on the equipment. Patient safety / Past Batches: At the time of nonconformance, protamine sulphate batch no. 523062 (2-8 ℃) was stored in the approved RM walk in cold room (E/WH/020) and Insulin crystal Human (R-DNA) batch no. RHI24063 and RHI24065 (-18 ℃ or below) and Insulin glargine (IP/Ph.Eur) batch no. RIG23003-RP (-20 ± 5) were stored in the approved RM walk in deep-freezer (E/WH/021). All stored materials accelerated stability data is available. Hence there is no impact on the patient safety/past batches. |  |  |  |
| Improve: Improve section covers the corrective actions Following checkpoint shall be considered while finalizing the corrective actions, - Were specific corrective Actions identified (including applicable Immediate Actions) to remediate the current issue or situation such that the associated system was returned to a state of control/compliance? - Were specific Corrective Actions identified for each root cause /substantiated probable root cause, as applicable? - Was the Corrective action assigned a unique number, responsible person and due date so it can be tracked? Does the action describe what will be the expected outcome they can be verified? - Was Effectiveness Verification required or not and the rationale for either documented based within the quality impact of the deviation after the investigation concluded? - Are the identified corrective actions achievable based on the information provided? |  |  |  |
| Corrective Action: |  |  |  |
| The investigation has been driven through 5 Why, Personal interview tools. During the investigation, personal interviews was carried out. Based on the detailed investigation, it has been concluded that, the nonconformance occurred to the tripping of the entire UPSDB-3 main incomer 63 Amps. causing a power disruption. Following corrective action has been identified based on the investigation outcome, - Awareness training on deviation (DEV/WH/24/004) shall be imparted to the concern persons. - Awareness training on ‘Breakdown and Work Order Procedure’ SOP no. SOP/DP/EU/003 shall be imparted to the concern person. CAPA form shall be initiated to track the corrective action with a unique number. Responsibilities and target completion date shall be mentioned in the CAPA form. The implementation outcome of corrective action shall be verified in CAPA form. The nonconformance pertains to temperature excursion and data loss of Approved RM walk-in cold room (Equipment ID: E/WH/020) and approved RM walk-in deep freezer (Equipment ID: E/WH/021) and proposed corrective action is related to the training, hence effectiveness verification is not required. Occurred deviation is related to the temperature and data loss and all stored materials accelerated stability data have available; therefore, impact have not been anticipated on material and testing/release. |  |  |  |
| Control: Control section covers the preventive actions Following checkpoint shall be considered while finalizing the preventive actions, - Were specific Preventive Actions identified for each root cause /substantiated probable root cause as applicable? - Was the Preventive Action linked the classification of the root cause and explanation given for how it will prevent recurrence? - Was the Preventive action assigned a unique number, responsible person and due date so it can be tracked? Does the action describe and expected outcome can be verified? - Was Effectiveness Verification required or not and the rationale for either documented based on the quality impact of the incident after the investigation concluded? - Was an Interim Plan needed to ensure a state the control while the Preventive Actions were implemented? - Was rationale provided when no Preventive Action were identified? - Does the Final Comments section include rotational to support the conclusion of the investigation and CAPA. - Was each of the impact assessment fields completed correctly - Regulatory Impact, Regulatory notification Product Quality, Validation, Stability, Market/Clinical? - Does the Recommended Lot disposition match the conclusions of the investigation and Impact assessment? - Does the Conclusion include final decision and rationale other regulatory notification required? - CAPA required to release material or batches have been verified to be complete and closed prior to material or batch disposition. Any related CAPA that remain open, but have no impact on the material or batch release and a documented explanation is provided. - Does the Conclusion include a brief summary of root cause, final scope/impact including rationale for product/material disposition, impact assessment and relevant lot/material/equipment details? - Are the identified preventive actions achievable based on the information provided? |  |  |  |
| Preventive Action: |  |  |  |
| The investigation has been carried out through 5 Why and Personal interview during the investigation probable root cause was identified as. As per outcome of the investigation following preventive action has been identified. - The cable coming from the UPS supply to be check for proper condition. - Separate UPS supply shall be provided for each cold room. CAPA form shall be initiated to track the preventive action with unique numbering. Responsibility and target completion date of identified preventive actions shall be assigned in CAPA form. The implementation Outcome of preventive action shall be verified in CAPA form. The nonconformance is isolated and categorized as minor and identified actions are related to the verification of UPS supply and provide the separate supply to each cold room, hence effectiveness monitoring shall not require. The preventive action shall be implemented after approval of CAPA, since the UPS power supply backup lasts for over 4 hours. Additionally, a 40 Amp MCB has been installed on each phase of UPSDB-3, which exceeds the actual load. Preventive action is related to the verification of UPS supply cable and provided to separate UPS supply to each cold room, hence interim control not required. The occurred deviation is related to temperature excursion and data loss of cold room and freezer room and root cause identified as equipment / instrument and electrical failure, hence no impact on product quality, validation, stability, market/clinical and testing/release of product and no any regulatory impact. The nonconformance is related to the temperature excursion and data loss of cold room and freezer room, there is no any impact to the products/materials, hence material or batch disposition impact not anticipated |  |  |  |
| Document Reviewed: |  |  |  |
| - SOP for operation and cleaning procedure for walk in cold room and walk in deep freezer. - Data Logs for both the equipment walk in cold room and walk in deep freezer - Equipment uses log |  |  |  |
| List of attachment (If applicable): |  |  |  |
| - Attachment No. I: Photograph of Damaged Cable - Attachment No. II: Record sheet for Personnel Interview of (Employee ID: 787) - Attachment No. III: Root cause categorization |  |  |  |

| Prepared By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date) | Reviewed By (Sign/Date | Approved By QA (Sign/Date) |
| --- | --- | --- | --- | --- | --- | --- |